## Analysis Inputs
Question | Answer | Possible Answers (must be exact) | Notes
Property Name | CWD | Any
What is the majority lease sturcture? | Mod Gross | Gross, Mod Gross, Triple Net
How does the percentage of common space to total space compare with other buildings? | Below Average | Above Average, Average, Below Average | Above Average (40-50%) Average (20-50%) Below Average (Less than 20%)
Is the existing HVAC system inefficient but not slotted for replacement | No | Yes or No
Is the HVAC system nearing its end of life? | No | Yes or No | Yes:System over 20 year old/planning to replace within 5 years No:System has at least 5 years of useabe life
Does the building have any of the following lighting: incandescent, halogen, standard metal halide, metal halide, T-12, mercury vapor? | Yes | Yes or No
Has there been a major renovation within the last 10 years? | Yes | Yes or No
Has the building had a commissioning in the last 5 years? | No | Yes or No
Does demand rate account for over 20%-55% of monthly utility bill? | Yes | Yes or No
Is the roof nearing replacement? | No | Yes or No
Criteria Weights (must sum to 100%)
Upfront Cost | 40%
Payback Period | 30%
Time Savings | 30%
Total | 100%
Factor in Effect on Demand Rate | Yes | Yes or No
Importance of Demand Rate Impact | Medium | High, Medium, Low
Note on D4: Look up exact percentages for what is above ave, ave, below ave -Ryan Moya

## Summary
Property Name | CWD
Technology | Property Specifc | Criteria Weighted | Total | Normalized Score (0-100)
Variable Frequency Drives | 14.16% | 15.53% | 32.69% | 98.4944
Occupancy Sensors | 10.73% | 17.46% | 33.19% | 100
HVAC Economizer | 14.16% | 11.73% | 29.39% | 88.5542
Building Management System | 9.013% | 15.51% | 24.53% | 73.8921
Variable Air Volume | 14.16% | 6.368% | 20.53% | 61.8545
LED Lighting | 9.013% | 8.236% | 20.25% | 61.0035
Weatherization | 12.45% | 9.039% | 21.49% | 64.7306
Old Boiler Replacement | 5.15% | 6.64% | 15.29% | 46.0648
Geothermal | 5.15% | 7.258% | 12.41% | 37.3821
Cool Roof | 6.009% | 2.223% | 8.232% | 24.7993

## Property Specific Score
Property |  |  | X
| Criteria |  | LED Lighting | Geothermal | Weather- ization | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement
Upfront Cost | High-$0-$5000 Medium-$5000
Payback Timeframe
Retrofit Capatability
Time Saver
Tenant Awareness/Approval
Assists Data Integration
Questions | Measurement | Criteria | LED Lighting | Geothermal | Building Envelop(i.e.Weather- ization) | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Building Sensors (i.e.Occupancy Sensors) | HVAC Economizer | Old Boiler Replacement
Most common lease structure | Gross Mod Gross Triple Net | High: Gross Med: Mod Gross Low: Triple Net | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low | If Gross: High If Mod Gros: Med If Triple Net : Low
| Mod Gross |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Amount of Common Space (Common SQFT/Total SQFT) | Above Average (40-50%) Average (20-50%) Below Average (Less than 20%) | High: (Above) Technology installed IN common space Med: (Above) Technology shares energy savings building-wide (Average) Technology installed IN common space Low: (Average) Technology shares energy savings building-wide NA: (Below) | If Above: High If Average: Med If Below: Low | If Above: Med If Average: Low If Below: NA | If Above: Med If Average: Low If Below: NA | If Above: Med If Average: Low If Below: NA | If Above: Med If Average: Low If Below: NA | If Above: Med If Average: Low If Below: NA | If Above: High If Average: Med If Below: Low | If Above: High If Average: Med If Below: Low | If Above: High If Average: Med If Below: Low | If Above: Med If Average: Low If Below: NA
| Below Average |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Is the existing HVAC system inefficient but not not slated for replacement? | Y/N | High: Improves the functionality of the HVAC system Med: Reduces heating and cooling demand with no effect on HVAC functionality Low: Would require new HVAC system, or has no impact on HVAC | If Yes: Low If No: NA | If Yes: Low If No: NA | If Yes: Med If No: NA | If Yes: Med If No: NA | If Yes: High If No: NA | If Yes: High If No: NA | If Yes: Med If No: NA | If Yes: Med If No: NA | If Yes: High If No: NA | If Yes: Low If No: NA
| No |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Is the HVAC system nearing end of life | Yes:System over 20 year old/planning to replace within 5 years No:System has at least 5 years of useabe life | High: (Yes) Viable HVAC replacement Med: (Yes) Reduces Heating and Cooling loads with no effect on HVAC functionality Low: (No) Applicable to HVAC even with replacement pending (No) Requirees HVAC replacement NA: (Yes/No) No impact on HVAC replacement | If Yes: NA If No: NA | If Yes: High If No: Low | If Yes: Med If No: Low | If Yes: Med If No: Low | If Yes: Med If No: Low | If Yes: Med If No: Low | If Yes: Med If No: Low | If Yes: NA If No: NA | If Yes: Med If No: Low | If Yes: High If No: Low
| No |  | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1
Do you have any of the following lighting: Incandescent, halogen, standard metal halide, metal halide, T-12, mercury vapor? | Y/N | High: Lighting replacement Med: Helps optimimize lighting useage NA: Not related to lights | If Yes: High If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: Med If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA
| Yes |  | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0
Was here a major renovation in the last 10 years? | Y/N | High: (No) Technology requires major rennovation Med: (No) Technology requires only modertate rennovation (Yes/No) Technology does not require property renovation Low: (Yes) Technology requires only modertate rennovation NA: (Yes) Technology requires major rennovation | If Yes: Low If No: Med | If Yes: NA If No: High | If Yes: Low If No: Med | If Yes: Low If No: Med | If Yes: Med If No: Med | If Yes: Med If No: Med | If Yes: Low If No: Med | If Yes: Low If No: Med | If Yes: Med If No: Med | If Yes: NA If No: High
| Yes |  | 1 | 0 | 1 | 1 | 5 | 5 | 1 | 1 | 5 | 0
Was the latest commissioning within 5 years? | Y/N | High: (No) Condition of technology can diminish significantly and unpredictably within 5 years Low: (No) Technology condition changes slowly and predictably or technology unlikely to have been recommended over 5 years ago NA: (Yes) | If Yes: NA If No: Low | If Yes: NA If No: Low | If Yes: NA If No: High | If Yes: NA If No: Low | If Yes: NA If No: High | If Yes: NA If No: High | If Yes: NA If No: Low | If Yes: NA If No: Low | If Yes: NA If No: High | If Yes: NA If No: Low
| No |  | 1 | 1 | 9 | 1 | 9 | 9 | 1 | 1 | 9 | 1
Does demand rate account for over 20%-55% of monthly utility bill? | Y/N | High: (Yes) Technologly enhances data capturing, energy optimization and/or shows where within building high consumption is occuring (i.e. hotspots) Low: (Yes) Technology reduces energy consumption NA: (No) | If Yes: Low If No: NA | If Yes: Low If No: NA | If Yes: High If No: NA | If Yes: Low If No: NA | If Yes: High If No: NA | If Yes: High If No: NA | If Yes: High If No: NA | If Yes: High If No: NA | If Yes: High If No: NA | If Yes: Low If No: NA
| Yes |  | 1 | 1 | 9 | 1 | 9 | 9 | 9 | 9 | 9 | 1
Is the roof nearing replacement | Y/N | High: (Yes) Techology is a roof Low: (No) Technology applies to an existing roof NA: (No/Yes): Technology not related to roof | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: High If No: Low | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA | If Yes: NA If No: NA
| No |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total | 21 | 12 | 29 | 14 | 33 | 33 | 21 | 25 | 33 | 12
|  | Normalized Score | 9.013% | 5.15% | 12.45% | 6.009% | 14.16% | 14.16% | 9.013% | 10.73% | 14.16% | 5.15% | 1
Note on B16: Look up exact percentages for what is above ave, ave, below ave -Ryan Moya

## Upfront Cost-Pairwise
Comparison Matrix
Upfront Cost | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement |  |  | Score | Criteria
LED Lighting | 1 | 3 | 0.2 | 3 | 0.14286 | 3 | 0.33333 | 0.14286 | 0.33333 | 5 | 16.1524 |  | 1 | A and B are equal
Geothermal | 0.33333 | 1 | 0.14286 | 1 | 0.2 | 0.33333 | 0.2 | 0.11111 | 0.2 | 3 | 6.5206 |  | 3 | A is thought to be moderately more prefered than B
Building Envelope | 5 | 6.9999 | 1 | 7 | 3 | 5 | 3 | 0.33333 | 3 | 9 | 43.3332 |  | 5 | A is thought to be strongly more prefered than B
Cool Roof | 0.33333 | 1 | 0.14286 | 1 | 0.2 | 0.33333 | 0.2 | 0.11111 | 0.2 | 3 | 6.5206 |  | 7 | A is thought to be or has demonstrated that it is much more prefered than B
Variable Frequency Drives | 6.9999 | 5 | 0.33333 | 5 | 1 | 5 | 5 | 0.14286 | 3 | 7 | 38.4761 |  | 9 | A can be emperically shown to be much more prefered than B
Variable Air Volume | 0.33333 | 3 | 0.2 | 3 | 0.2 | 1 | 0.2 | 0.14286 | 0.2 | 5 | 13.2763 |  |  | Preference signifies lower upfront cost
Building Management System | 3 | 5 | 0.33333 | 5 | 0.2 | 5 | 1 | 0.33333 | 3 | 7 | 29.8667
Occupancy Sensors | 6.9999 | 9.0001 | 3 | 9.0001 | 6.9999 | 6.9999 | 3 | 1 | 5 | 9 | 59.9998
HVAC Economizer | 3 | 5 | 0.33333 | 5 | 0.33333 | 5 | 0.33333 | 0.2 | 1 | 9 | 29.2
Old Boiler Replacement | 0.2 | 0.33333 | 0.11111 | 0.33333 | 0.14286 | 0.2 | 0.14286 | 0.11111 | 0.11111 | 1 | 2.6857
0
Total | 27.1998 | 39.3333 | 5.7969 | 39.3335 | 12.4189 | 31.8665 | 13.4096 | 2.6286 | 16.0444 | 58 | 246.0314
Normalized Matrix
Upfront Cost | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement | Average Criteria Weights (W)
LED Lighting | 0.036765 | 0.076271 | 0.034501 | 0.076271 | 0.011503 | 0.094143 | 0.024858 | 0.054349 | 0.020775 | 0.086207 | 0.051564
Geothermal | 0.012255 | 0.025424 | 0.024644 | 0.025424 | 0.016104 | 0.01046 | 0.014915 | 0.04227 | 0.012465 | 0.051724 | 0.023569
Building Envelope | 0.18383 | 0.17796 | 0.17251 | 0.17797 | 0.24157 | 0.1569 | 0.22372 | 0.12681 | 0.18698 | 0.15517 | 0.18034
Cool Roof | 0.012255 | 0.025424 | 0.024644 | 0.025424 | 0.016104 | 0.01046 | 0.014915 | 0.04227 | 0.012465 | 0.051724 | 0.023569
Variable Frequency Drives | 0.25735 | 0.12712 | 0.057502 | 0.12712 | 0.080522 | 0.1569 | 0.37287 | 0.054349 | 0.18698 | 0.12069 | 0.15414
Variable Air Volume | 0.012255 | 0.076272 | 0.034501 | 0.076272 | 0.016104 | 0.031381 | 0.014915 | 0.054349 | 0.012465 | 0.086207 | 0.041472
Building Management System | 0.1103 | 0.12712 | 0.057502 | 0.12712 | 0.016104 | 0.1569 | 0.074574 | 0.12681 | 0.18698 | 0.12069 | 0.11041
Occupancy Sensors | 0.25735 | 0.22882 | 0.51753 | 0.22882 | 0.56365 | 0.21966 | 0.22372 | 0.38043 | 0.31163 | 0.15517 | 0.30868
HVAC Economizer | 0.1103 | 0.12712 | 0.057502 | 0.12712 | 0.026841 | 0.1569 | 0.024858 | 0.076087 | 0.062327 | 0.15517 | 0.092422
Old Boiler Replacement | 0.007353 | 0.0084746 | 0.019167 | 0.0084746 | 0.011503 | 0.0062762 | 0.010653 | 0.042271 | 0.0069252 | 0.017241 | 0.013834
Total | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Consistancy Score
Upfront Cost | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement | Sum | Sum/Weight
LED Lighting | 0.051564 | 0.070706 | 0.036068 | 0.070706 | 0.02202 | 0.12442 | 0.036803 | 0.044098 | 0.030807 | 0.06917 | 0.55636 | 10.7896
Geothermal | 0.017188 | 0.023569 | 0.025764 | 0.023569 | 0.030828 | 0.013824 | 0.022082 | 0.034297 | 0.018484 | 0.041502 | 0.25111 | 10.6543
Building Envelope | 0.25782 | 0.16498 | 0.18034 | 0.16498 | 0.46242 | 0.20736 | 0.33123 | 0.10289 | 0.27727 | 0.12451 | 2.2738 | 12.6083
Cool Roof | 0.017188 | 0.023569 | 0.025763 | 0.023569 | 0.030828 | 0.013824 | 0.022082 | 0.034297 | 0.018484 | 0.041502 | 0.25111 | 10.6543
Variable Frequency Drives | 0.36094 | 0.11784 | 0.060114 | 0.11784 | 0.15414 | 0.20736 | 0.55205 | 0.044098 | 0.27727 | 0.096838 | 1.9885 | 12.9006
Variable Air Volume | 0.017188 | 0.070706 | 0.036068 | 0.070706 | 0.030828 | 0.041472 | 0.022082 | 0.044098 | 0.018484 | 0.06917 | 0.4208 | 10.1467
Building Management System | 0.15469 | 0.11784 | 0.060114 | 0.11784 | 0.030828 | 0.20736 | 0.11041 | 0.10289 | 0.27727 | 0.096838 | 1.2761 | 11.5577
Occupancy Sensors | 0.36094 | 0.21212 | 0.54103 | 0.21212 | 1.079 | 0.2903 | 0.33123 | 0.30868 | 0.46211 | 0.12451 | 3.922 | 12.7058
HVAC Economizer | 0.15469 | 0.11784 | 0.060114 | 0.11784 | 0.05138 | 0.20736 | 0.036803 | 0.061736 | 0.092422 | 0.12451 | 1.0247 | 11.0871
Old Boiler Replacement | 0.010313 | 0.0078562 | 0.020038 | 0.0078562 | 0.02202 | 0.0082944 | 0.015773 | 0.034298 | 0.010269 | 0.013834 | 0.15055 | 10.8827
Technology Count | 10
Lamda Max | 11.3987
Consistancy Index | 0.15541
Random Index (n=10) | 1.49
Consistancy Ratio | 0.1043

## Payback Period-Pairwise
Comparison Matrix
Payback Period | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement |  |  | Score | Criteria
LED Lighting | 1 | 7 | 5 | 7 | 0.14286 | 0.33333 | 0.33333 | 0.33333 | 0.14286 | 5 | 26.2857 |  | 1 | A and B are equal
Geothermal | 0.14286 | 1 | 0.2 | 1 | 0.11111 | 0.14286 | 0.14286 | 0.14286 | 0.11111 | 1 | 3.9937 |  | 3 | A is thought to be moderately more prefered than B
Building Envelope | 0.2 | 5 | 1 | 7 | 0.14286 | 0.2 | 0.33333 | 0.2 | 0.14286 | 3 | 17.219 |  | 5 | A is thought to be strongly more prefered than B
Cool Roof | 0.14286 | 1 | 0.14286 | 1 | 0.11111 | 0.14286 | 0.14286 | 0.11111 | 0.11111 | 1 | 3.9048 |  | 7 | A is thought to be or has demonstrated that it is much more prefered than B
Variable Frequency Drives | 6.9999 | 9.0001 | 6.9999 | 9.0001 | 1 | 3 | 5 | 3 | 1 | 9 | 53.9999 |  | 9 | A can be emperically shown to be much more prefered than B
Variable Air Volume | 3 | 6.9999 | 5 | 6.9999 | 0.33333 | 1 | 3 | 3 | 0.33333 | 7 | 36.6664 |  |  | Preference based on shorter payback period
Building Management System | 3 | 6.9999 | 3 | 6.9999 | 0.2 | 0.33333 | 1 | 0.33333 | 0.33333 | 7 | 29.1998
Occupancy Sensors | 3 | 6.9999 | 5 | 9.0001 | 0.33333 | 0.33333 | 3 | 1 | 0.33333 | 9 | 38
HVAC Economizer | 6.9999 | 9.0001 | 6.9999 | 9.0001 | 1 | 3 | 3 | 3 | 1 | 9 | 52
Old Boiler Replacement | 0.2 | 1 | 0.33333 | 1 | 0.11111 | 0.14286 | 0.14286 | 0.11111 | 0.11111 | 1 | 4.1524
Total | 24.6855 | 53.9998 | 33.6759 | 58 | 3.4857 | 8.6286 | 16.0953 | 11.2318 | 3.619 | 52 | 265.4216
Normalized Matrix
Payback Period | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement | Average Criteria Weights (W)
LED Lighting | 0.04051 | 0.12963 | 0.14847 | 0.12069 | 0.040984 | 0.038631 | 0.02071 | 0.029677 | 0.039475 | 0.096154 | 0.070493
Geothermal | 0.0057871 | 0.018519 | 0.005939 | 0.017241 | 0.031876 | 0.016557 | 0.0088759 | 0.012719 | 0.030702 | 0.019231 | 0.016745
Building Envelope | 0.0081019 | 0.092593 | 0.029695 | 0.12069 | 0.040984 | 0.023179 | 0.02071 | 0.017807 | 0.039475 | 0.057692 | 0.045093
Cool Roof | 0.0057871 | 0.018519 | 0.0042421 | 0.017241 | 0.031876 | 0.016557 | 0.0088759 | 0.0098925 | 0.030702 | 0.019231 | 0.016292
Variable Frequency Drives | 0.28356 | 0.16667 | 0.20786 | 0.15517 | 0.28688 | 0.34768 | 0.31065 | 0.2671 | 0.27632 | 0.17308 | 0.2475
Variable Air Volume | 0.12153 | 0.12963 | 0.14847 | 0.12069 | 0.095628 | 0.11589 | 0.18639 | 0.2671 | 0.092105 | 0.13462 | 0.1412
Building Management System | 0.12153 | 0.12963 | 0.089085 | 0.12069 | 0.057377 | 0.038631 | 0.06213 | 0.029677 | 0.092105 | 0.13462 | 0.087547
Occupancy Sensors | 0.12153 | 0.12963 | 0.14847 | 0.15517 | 0.095628 | 0.038631 | 0.18639 | 0.089033 | 0.092105 | 0.17308 | 0.12297
HVAC Economizer | 0.28356 | 0.16667 | 0.20786 | 0.15517 | 0.28688 | 0.34768 | 0.18639 | 0.2671 | 0.27632 | 0.17308 | 0.23507
Old Boiler Replacement | 0.0081019 | 0.018519 | 0.0098983 | 0.017241 | 0.031876 | 0.016556 | 0.0088757 | 0.0098926 | 0.030702 | 0.019231 | 0.017089
Total | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Consistancy Score
Upfront Cost | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement | Sum | Sum/Weight
LED Lighting | 0.070493 | 0.11721 | 0.22546 | 0.11405 | 0.035357 | 0.047068 | 0.029182 | 0.040989 | 0.033582 | 0.085447 | 0.79884 | 11.3321
Geothermal | 0.01007 | 0.016745 | 0.0090185 | 0.016292 | 0.027499 | 0.020173 | 0.012507 | 0.017567 | 0.026119 | 0.017089 | 0.17308 | 10.3365
Building Envelope | 0.014099 | 0.083723 | 0.045093 | 0.11405 | 0.035357 | 0.028241 | 0.029182 | 0.024593 | 0.033582 | 0.051268 | 0.45918 | 10.1831
Cool Roof | 0.01007 | 0.016745 | 0.0064418 | 0.016292 | 0.027499 | 0.020173 | 0.012507 | 0.013663 | 0.026119 | 0.017089 | 0.1666 | 10.2257
Variable Frequency Drives | 0.49344 | 0.1507 | 0.31564 | 0.14663 | 0.2475 | 0.42361 | 0.43773 | 0.3689 | 0.23507 | 0.1538 | 2.973 | 12.0124
Variable Air Volume | 0.21148 | 0.11721 | 0.22546 | 0.11404 | 0.082499 | 0.1412 | 0.26264 | 0.3689 | 0.078357 | 0.11963 | 1.7214 | 12.191
Building Management System | 0.21148 | 0.11721 | 0.13528 | 0.11404 | 0.049499 | 0.047068 | 0.087547 | 0.040989 | 0.078357 | 0.11963 | 1.0011 | 11.4351
Occupancy Sensors | 0.21148 | 0.11721 | 0.22546 | 0.14663 | 0.082499 | 0.047068 | 0.26264 | 0.12297 | 0.078357 | 0.1538 | 1.4481 | 11.7765
HVAC Economizer | 0.49344 | 0.1507 | 0.31564 | 0.14663 | 0.2475 | 0.42362 | 0.26264 | 0.36891 | 0.23507 | 0.1538 | 2.798 | 11.9026
Old Boiler Replacement | 0.014099 | 0.016745 | 0.015031 | 0.016292 | 0.0275 | 0.020172 | 0.012507 | 0.013663 | 0.026119 | 0.017089 | 0.17922 | 10.487
Technology Count | 10
Lamda Max | 11.1882
Consistancy Index | 0.13202
Random Index (n=10) | 1.49
Consistancy Ratio | 0.088605

## Time Saving-Pairwise
Comparison Matrix
Time Saving | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement |  |  | Score | Criteria
LED Lighting | 1 | 0.33333 | 9 | 7 | 5 | 9 | 0.33333 | 5 | 7 | 0.33333 | 44 |  | 1 | A and B are equal
Geothermal | 3 | 1 | 9 | 7 | 5 | 9 | 0.33333 | 5 | 5 | 3 | 47.3333 |  | 3 | A is thought to be moderately more prefered than B
Building Envelope | 0.11111 | 0.11111 | 1 | 0.33333 | 0.2 | 1 | 0.11111 | 0.33333 | 0.33333 | 0.11111 | 3.6444 |  | 5 | A is thought to be strongly more prefered than B
Cool Roof | 0.14286 | 0.14286 | 3 | 1 | 0.33333 | 3 | 0.11111 | 0.33333 | 0.33333 | 0.11111 | 8.5079 |  | 7 | A is thought to be or has demonstrated that it is much more prefered than B
Variable Frequency Drives | 0.2 | 0.2 | 5 | 3 | 1 | 5 | 0.14286 | 3 | 5 | 0.14286 | 22.6857 |  | 9 | A can be emperically shown to be much more prefered than B
Variable Air Volume | 0.11111 | 0.11111 | 1 | 0.33333 | 0.2 | 1 | 0.11111 | 0.33333 | 0.33333 | 0.11111 | 3.6444 |  |  | Preferance signifies more time saved for maintenance staff
Building Management System | 3 | 3 | 9 | 9 | 7 | 9 | 1 | 7 | 9 | 3 | 60
Occupancy Sensors | 0.2 | 0.2 | 3 | 3 | 0.33333 | 3 | 0.14286 | 1 | 5 | 0.14286 | 16.0191
HVAC Economizer | 0.14286 | 0.2 | 3 | 3 | 0.2 | 3 | 0.11111 | 0.2 | 1 | 0.11111 | 10.9651
Old Boiler Replacement | 3 | 0.33333 | 9 | 9 | 7 | 9 | 0.33333 | 7 | 9 | 1 | 54.6667
Total | 10.9079 | 5.6317 | 52 | 42.6667 | 26.2667 | 52 | 2.7302 | 29.2 | 42 | 8.0635 | 271.4668
Normalized Matrix
Time Saving | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement | Average Criteria Weights (W)
LED Lighting | 0.091676 | 0.059188 | 0.17308 | 0.16406 | 0.19036 | 0.17308 | 0.12209 | 0.17123 | 0.16667 | 0.041339 | 0.13528
Geothermal | 0.27503 | 0.17756 | 0.17308 | 0.16406 | 0.19036 | 0.17308 | 0.12209 | 0.17123 | 0.11905 | 0.37205 | 0.19376
Building Envelope | 0.010186 | 0.019729 | 0.019231 | 0.0078125 | 0.0076142 | 0.019231 | 0.040698 | 0.011416 | 0.0079365 | 0.01378 | 0.015763
Cool Roof | 0.013097 | 0.025366 | 0.057692 | 0.023437 | 0.01269 | 0.057692 | 0.040698 | 0.011416 | 0.0079365 | 0.01378 | 0.02638
Variable Frequency Drives | 0.018335 | 0.035513 | 0.096154 | 0.070313 | 0.038071 | 0.096154 | 0.052326 | 0.10274 | 0.11905 | 0.017717 | 0.064637
Variable Air Volume | 0.010186 | 0.019729 | 0.019231 | 0.0078125 | 0.0076142 | 0.019231 | 0.040698 | 0.011416 | 0.0079365 | 0.01378 | 0.015763
Building Management System | 0.27503 | 0.53269 | 0.17308 | 0.21094 | 0.2665 | 0.17308 | 0.36628 | 0.23973 | 0.21429 | 0.37205 | 0.28237
Occupancy Sensors | 0.018335 | 0.035513 | 0.057692 | 0.070313 | 0.01269 | 0.057692 | 0.052326 | 0.034247 | 0.11905 | 0.017717 | 0.047557
HVAC Economizer | 0.013097 | 0.035513 | 0.057692 | 0.070313 | 0.0076142 | 0.057692 | 0.040698 | 0.0068493 | 0.02381 | 0.01378 | 0.032706
Old Boiler Replacement | 0.27503 | 0.059188 | 0.17308 | 0.21094 | 0.2665 | 0.17308 | 0.12209 | 0.23973 | 0.21429 | 0.12402 | 0.18579
Total | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Consistancy Score
Time Saving | LED Lighting | Geothermal | Building Envelope | Cool Roof | Variable Frequency Drives | Variable Air Volume | Building Management System | Occupancy Sensors | HVAC Economizer | Old Boiler Replacement | Sum | Sum/Weight
LED Lighting | 0.13528 | 0.064586 | 0.14187 | 0.18466 | 0.32318 | 0.14187 | 0.094122 | 0.23779 | 0.22894 | 0.061931 | 1.6142 | 11.9328
Geothermal | 0.40583 | 0.19376 | 0.14187 | 0.18466 | 0.32318 | 0.14187 | 0.094122 | 0.23779 | 0.16353 | 0.55738 | 2.444 | 12.6136
Building Envelope | 0.015031 | 0.021529 | 0.015763 | 0.0087935 | 0.012927 | 0.015763 | 0.031374 | 0.015852 | 0.010902 | 0.020644 | 0.16858 | 10.6944
Cool Roof | 0.019325 | 0.02768 | 0.04729 | 0.02638 | 0.021546 | 0.04729 | 0.031374 | 0.015852 | 0.010902 | 0.020644 | 0.26828 | 10.1698
Variable Frequency Drives | 0.027055 | 0.038752 | 0.078817 | 0.079141 | 0.064637 | 0.078817 | 0.040338 | 0.14267 | 0.16353 | 0.026542 | 0.7403 | 11.4532
Variable Air Volume | 0.015031 | 0.021529 | 0.015763 | 0.0087935 | 0.012927 | 0.015763 | 0.031374 | 0.015852 | 0.010902 | 0.020644 | 0.16858 | 10.6944
Building Management System | 0.40583 | 0.58128 | 0.14187 | 0.23742 | 0.45246 | 0.14187 | 0.28237 | 0.3329 | 0.29435 | 0.55738 | 3.4277 | 12.1393
Occupancy Sensors | 0.027055 | 0.038752 | 0.04729 | 0.079141 | 0.021546 | 0.04729 | 0.040338 | 0.047557 | 0.16353 | 0.026542 | 0.53904 | 11.3345
HVAC Economizer | 0.019325 | 0.038752 | 0.04729 | 0.079141 | 0.012927 | 0.04729 | 0.031374 | 0.0095114 | 0.032706 | 0.020644 | 0.33896 | 10.364
Old Boiler Replacement | 0.40583 | 0.064586 | 0.14187 | 0.23742 | 0.45246 | 0.14187 | 0.094122 | 0.3329 | 0.29435 | 0.18579 | 2.3512 | 12.655
Technology Count | 10
Lamda Max | 11.4051
Consistancy Index | 0.15612
Random Index (n=10) | 1.49
Consistancy Ratio | 0.10478

## Pairwise Evaluation Sources
Technology | Upfront Cost Weight | Payback Period Weight | Time Savings Weight | Weighted Average
LED Lighting | 0.051564 | 0.070493 | 0.13528 | 0.082357 | A | Infrequent | Frequent
Geothermal | 0.023569 | 0.016745 | 0.19376 | 0.072578 | Predictable | Low | Med-2
Weatherization | 0.18034 | 0.045093 | 0.015763 | 0.090393 | Unpredictable | Med-1 | High
Cool Roof | 0.023569 | 0.016292 | 0.02638 | 0.022229
Variable Frequency Drives | 0.15414 | 0.2475 | 0.064637 | 0.1553 | B | Quick Fix | Delayed Fix
Variable Air Volume | 0.041472 | 0.1412 | 0.015763 | 0.063679 | In House | Low | Med-2
Building Management System | 0.11041 | 0.087547 | 0.28237 | 0.15514 | Contract | Med-1 | High
Occupancy Sensors | 0.30868 | 0.12297 | 0.047557 | 0.17463
HVAC Economizer | 0.092422 | 0.23507 | 0.032706 | 0.1173
Old Boiler Replacement | 0.013834 | 0.017089 | 0.18579 | 0.066398

## Demand Rate
Technology | Demand Rate Savings Potential (RANK 1-5; 5=Best & 1=Worst ) | Score | Percentage of Max Score | Multiplier
LED Lighting | 3 | 3 | 60% | 0.03
Geothermal | 2.5 | 0 | 0% | 0
Building Envelope | 2 | 0 | 0% | 0
Cool Roof | 2.5 | 0 | 0% | 0
Variable Frequency Drives | 3 | 3 | 60% | 0.03
Variable Air Volume | 2 | 0 | 0% | 0
Building Management System | 1 | 0 | 0% | 0
Occupancy Sensors | 5 | 5 | 100% | 0.05
HVAC Economizer | 3.5 | 3.5 | 70% | 0.035
Old Boiler Replacement | 3.5 | 3.5 | 70% | 0.035
|  |  |  | Max Multiplier Value | Demand Rate Impact Considered (1=yes, 0=no)
|  |  |  | 0.05 | 1

## Sheet1
HVAC efficiencies | No, largely assumed in other investment alternatives considered (VAV, VFDs, Economisers) |  | HVAC systems represent a significant portion of a building's energy consumption - 51% on average in commercial buildings in the U.S. (36% heating, 7% ventilation, 8% cooling) | Source: Energy Information Administration, "Commercial Buildings Energy Consumption Survey (CBECS): Table EIA. Major Fuel Consumption (BTU) by End Use for All Buildings," September 2008. Accessible at http://www.eia.doe.gov/emeu/cbecs/cbecs2003/detailed_tables_2003/detailed_tables_2003.html ) | Yes
Smart/Effiencient Appliances (refridgeration, water heater, TV, etc) | No, the savings will be primarily realized by the tenant in a triple net lease. | Danny | Appliances that use minimal energy and/or communicate with the grid in order to avoid using unnecessary energy during peak hours

## Sheet2
Upfront Cost
Occupancy Sensors | 28.9%
Building Envelope | 16.23%
Building Management System | 13.62%
Variable Frequency Drives | 12.9%
HVAC Economizer | 9.65%
LED Lighting | 5.322%
Variable Air Volume | 4.862%
Geothermal | 3.251%
Cool Roof | 3.251%
Old Boiler Replacement | 2.007%
Consistancy Ratio | 10.4%
Payback Period
Variable Frequency Drives | 24.75%
HVAC Economizer | 23.51%
Variable Air Volume | 14.12%
Occupancy Sensors | 12.3%
Building Management System | 8.755%
LED Lighting | 7.049%
Building Envelope | 4.509%
Old Boiler Replacement | 1.709%
Geothermal | 1.674%
Cool Roof | 1.629%
Consistancy Ratio | 8.861%
Time Savings
Building Management System | 28.24%
Geothermal | 19.38%
Old Boiler Replacement | 18.58%
LED Lighting | 13.53%
Variable Frequency Drives | 6.464%
Occupancy Sensors | 4.756%
HVAC Economizer | 3.271%
Cool Roof | 2.638%
Variable Air Volume | 1.576%
Building Envelope | 1.576%
Consistancy Ratio | 10.48%